## Slide 1
Co- PIs:
  Farhang Shadman, Chem and Environ Eng, UA
  Carl Geisert, Sr. Principal Engineer, Intel
Graduate Students:
  Jivaan Kishore: Ph.D. student, Chem Eng, UA
Undergraduate Students:
  Andrew Jimenez, Chem and Environ Eng, UA
Application of PCP in Drying Down UHP Gas Distribution Systems and Tools
Customized Project, Sponsored by Intel

## Slide 2
Objective
Contamination of gas distribution systems during operation or at start-up results in wasting of expensive UHP gases and valuable tool operation time.
Motivation and ESH Impact
Develop techniques for reducing UHP gas usage in fabs:
  Novel purge methods to remove contaminants during steady operation, start-ups, or recovery from system upsets.

## Slide 3
Multistage Gas
Purifier System
MFC 2
MFC 3
APIMS
CRDS
Houseline N2
Moisture Permeation Tube
P
Flow-restrictor (optional)
P
MFC 4
Gas Delivery System
Analyzers
2-way Valve
Gas distribution systems with different sizes and geometries were fabricated and provided by Intel
CRDS: high ppt – low ppm
APIMS: low ppt – low ppb
Experiment Testbed
A
B
C
Simulated process tool (interchangeable)
Capped lateral (interchangeable)
Vented lateral w/ orifice (interchangeable)
LaserTrace

## Slide 4
Comprehensive Simulator
Continuity equation:
Momentum balance:
Moisture concentration on the pipe surface:
Surface Diffusion
Adsorption and desorption
Adsorption and desorption
Convection
Moisture concentration in the gas phase:
Diffusion

## Slide 5
Purge Techniques
Pressure
Purge Time
SSP
SSP
DP
DP
DP
RP
RP
RP
Pressure
Purge Time
SSP
High Pressure
High Pressure
Low Pressure
Steady State Purge (SSP)
Pressure Cycle Purge (PCP)

## Slide 6
Example for Application of PCP:
Dry-Down of a Tool Chamber
Parameters of EPSS distribution line | 
Length of Main | 5 m
Length of Lateral | 1 m
Purge gas concentration | 0.2ppb
Initial surface concentration | 1E-6 mol/m^2
Surface capacity | 1.06E-6 mol/m^2
Lower operating pressure | 148000 Pa
Higher operating pressure | 640000 Pa
Time in low-pressure stage | 10 s
Time in high-pressure stage | 15 s
Depressurization time | 40 s
Adsorption rate constant | 500 m^3/(mol*s)
Desorption rate constant | 0.05 1/s
Orifice loss coefficient | 1E6
Valve close
Valve open
(reduced flow rate)
Valve open
Time (s)
Pressure (Pa)
Lateral
Main section

## Slide 7
Simulator Validation

## Slide 8
Surface Cleaning – PCP vs SSP

## Slide 9
Velocity profile – PCP vs SSP

## Slide 10
Dry Down Comparison of Varying Lateral Lenghts

## Slide 11
Purge Gas Saving with PCP

## Slide 12
Purging of Multiple Dead Volumes

## Slide 13
Purge Gas Savings with System Complexity

## Slide 14
Effect of Holding Times on Purge Rate

## Slide 15
Effect of Operating Pressure Range on Cyclic Purge

## Slide 16: Pressure Cyclic Purge (PCP) for Purging Tool Chambers
Lower Gas Usage + Lower Down Time
Means
ESH Gain + Lower Cost
Purging tool chambers (outgassing and removal of adsorbed impurities such as moisture) is a major user of expensive UHP gases and other resources.

## Slide 17
Point A
Point B
Conventional Steady State Purge (SSP)
SSP Flow Pattern
Point B
Point A
Darker regions: High concentration

## Slide 18: Conventional Steady State Purge (SSP)

## Slide 19: Conventional Steady State Purge (SSP)

## Slide 20: Conventional Steady State Purge (SSP)

## Slide 21: Pressure Cyclic Purge (PCP)
Velocity vectors
during PCP depressurization
Phigh
Plow
A open
B closed
A closed
B closed
A closed
B open
A closed
B closed
PCP-induced
convection in dead spaces
Valve B
Valve A

## Slide 22: Overall Chamber Cleaning Profiles
PCP
SSP
Average Surface Concentration (molecules/cm2)
Time (min)

## Slide 23: Surface Cleaning: PCP vs SSP
A
B
PCP
SSP
B
A
A
B
Point A
Point B
1.19E15 molecules/cm2
(Equilibrium gas-phase concentration = 15ppb)
Time (min)

## Slide 24: PCP Simulation
PCP Concentration Map

## Slide 25: PCP Simulation
PCP Concentration Map
PCP Concentration Map
LOW PRESSURE STAGE
Desoption from walls
HIGH PRESSURE STAGE
VENTING
LOW PRESSURE STAGE
DESOPRTION

## Slide 26: Purge Time Saving by PCP
Chart: Surface Concentration (molecules/cm^2)
| 5663969547788679 | 4719410178419973 | 3461142386687108 | 2202642894133709.5 | 1189543153479490.7
Point A | 4.2941 | 3.6714 | 3.7477 | 3.8367 | 4.0947
Point B | 6.1538 | 4.575 | 5.4417 | 5.8007 | 6.2225
Target concentration: 1.19E15 molecules/cm2
A
B
Point A
Point B

## Slide 27
Summary and Conclusions
A combination of experiments and process modelling was used to study the application of pressure cycling purge of gas distribution lines and system tools
The basis of the cleaning effect of PCP is identified as the induction of a beneficial convective flow in regions that do not see flow during conventional SSP purge.
Higher benefit of PCP over conventional SSP is realized with increasing system complexity and system size
Purge time and purge gas usage required to achieve a certain overall system cleanliness significantly reduces as a more stringent target concentration is desired
The process simulator can be used both for design and purging of a new gas distribution networks as well as for the efficient operation and dry-down of existing systems.

## Slide 28
  Continue joint work with Intel; some technology transfer and implementation of results at Intel fabs have already taken place.
  Process simulator was requested by and sent to AMAT
  Comprehensive version of purge simulator for distribution systems is available and ongoing work on tool chamber purge will be available by end of Fall 2014
Industrial Interactions
Roy Dittler, Jivaan Jhothiraman, Carl Geisert, Farhang Shadman. “Contamination of Ultra-High-Purity (UHP) Gas Distribution Systems by Back Diffusion of Impurities.” Journal of the IEST
Hao Wang, H. and Shadman, F. “Effect of Particle Size on the Adsorption and Desorption Properties of Oxide Nanoparticles” AIChE Journal 59(5), 1502 (2013).
Publications and Presentations

## Slide 29
  Carl Geisert (Intel)
  Gopal Rao (Formerly at Intel and SEMATECH)
  Roy Dittler (Intel)
  Junpin Yao (Matheson Tri-Gas)
  Hao Wang (ASM)
  Tiger Optics (major financial support and technical assistance)
Acknowledgements